## Certificate of Calibration
ΠΙΣΤΟΠΟΙΗΤΙΚΟ ΕΛΕΓΧΟΥ/ΔΙΑΚΡΙΒΩΣΗΣ ΟΡΓΑΝΟΥ
CERTIFICATE OF INSPECTION/CALIBRATION
Tag No |  | : | 15AT801 | [8 empty] | Manufacturer |  |  |  | : |  | Rosemount
[12 empty] | Model No |  |  |  | : |  | 3051
Service Description |  | : | FUEL GAS FROM V-1502 (H2S) | [8 empty] | Serial No |  |  |  | :
[12 empty] | Accuracy (% of span) |  |  |  | : |  | 0.075
[12 empty] | Range |  |  |  | : |  | 0 | - | 5000 | mmH2O
1. INSTRUMENT VISUAL CHECK
Instrument Type |  |  |  |  | : |  | DP Transmitter (Flow) |  |  |  | Process Connection |  |  |  |  | : |  | TUBING
Equipment |  |  |  |  | : |  | NO |  |  |  | Dimensions |  |  |  |  | : |  | 12 mm
Interval (days) |  |  |  |  | : |  | YES |  |  |  | Enclosure Rating / ATEX |  |  |  |  | : |  | Ex d IIC
Output Signal |  |  |  |  | : |  | mA |  |  |  | Cable |  |  |  |  | : |  | 1x2x1,3 armoured
2. FIELD CALIBRATION RECORD
2a. BEFORE CALIBRATION | [11 empty] | 2b. AFTER CALIBRATION
INPUT |  |  |  | OUTPUT |  |  |  | % Error |  |  |  | INPUT |  |  |  | OUTPUT |  |  |  | % Error
|  | 0 | % | 4 |  | mA | [7 empty] | 0 | % | 4 |  | mA
|  | 25 | % | 8 |  | mA | [7 empty] | 25 | % | 8 |  | mA
|  | 50 | % | 12 |  | mA | [7 empty] | 50 | % | 12 |  | mA
|  | 75 | % | 16.01 |  | mA | [7 empty] | 75 | % | 16 |  | mA
|  | 100 | % | 20.01 |  | mA | [7 empty] | 100 | % | 20 |  | mA
Linearity : |  |  | PASS |  | X |  | REJECT |  |  |  |  | Linearity : |  |  | PASS |  | X |  | REJECT
Repeatability : |  |  | PASS |  | X |  | REJECT |  |  |  |  | Repeatability : |  |  | PASS |  | X |  | REJECT
Test Equipment Used | [7 empty] | : | [5 empty] | Cal. Certificate |  |  |  | :
[14 empty] | Cal. Certificate |  |  |  | :
Test Equipment Calibration Validity | [7 empty] | :
Test Equipment Range | [7 empty] | :
3. INSTALLATION INSPECTION REPORT
| Manifold Correct |  |  | YES |  |  |  |  | Cable Glanded |  |  |  | YES |  | Area Classification
| Ferrules Correct |  |  | YES |  |  |  |  | Cable Cores Terminated |  |  |  | YES |  | Division/Zone |  |  | : | Zone 1
| Mounting Correct |  |  | YES |  |  |  |  | Cable Tag Installed |  |  |  | YES
| Fixings Secure |  |  | YES |  |  |  |  | Cable Shroud Fitted |  |  |  | YES | The installation is correct and ready for operation
| Tag Fitted |  |  | YES |  |  |  |  | S/S Tube Clipped |  |  |  | YES | [7 empty] | YES
COMMENTS
mmmmmmmmmm
4. CALIBRATION
[6 empty] | Date |  |  |  | Name | [5 empty] | Signature
Contractor | [5 empty] | 2022-09-02 |  |  |  | KAPOIOS
WE